{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["设备一览表"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"设备一览表","index":0,"n_rows":57,"n_cols":16,"rows_kept":57,"merged":[[0,0,0,1],[0,4,0,10],[1,0,2,0],[1,1,2,1],[1,2,2,2],[1,3,2,3],[1,4,2,4],[1,5,2,5],[1,6,2,6],[1,7,1,9],[1,10,2,10],[1,11,1,12],[1,13,2,13],[1,14,2,14],[1,15,2,15],[3,0,3,2],[4,1,4,2],[4,3,4,4],[4,15,22,15],[5,3,5,4],[6,3,6,4],[7,3,7,4],[8,3,8,4],[9,3,9,4],[10,1,10,2],[10,3,10,4],[11,3,11,4],[12,3,12,4],[13,3,13,4],[14,3,14,4],[15,3,15,4],[16,1,16,2],[16,3,16,4],[17,3,17,4],[18,3,18,4],[19,3,19,4],[20,3,20,4],[21,3,21,4],[22,3,22,4],[23,1,23,4],[24,1,24,2],[24,3,24,4],[25,3,25,4],[26,3,26,4],[27,3,27,4],[28,3,28,4],[29,3,29,4],[30,1,30,2],[30,3,30,4],[30,5,31,5],[31,3,31,4],[32,3,32,4],[33,3,33,4],[34,3,34,4],[35,3,35,4],[36,3,36,4],[37,3,37,4],[38,1,38,2],[38,3,38,4],[38,15,42,15],[39,3,39,4],[40,3,40,4],[41,3,41,4],[42,3,42,4],[43,1,43,2],[43,3,43,4],[43,15,48,15],[44,3,44,4],[45,3,45,4],[46,3,46,4],[47,3,47,4],[48,3,48,4],[49,1,49,2],[49,3,49,4],[50,3,50,4],[51,3,51,4],[52,1,52,4],[53,3,53,4],[54,3,54,4],[55,3,55,4],[56,3,56,4],[57,3,57,4]],"flags":["formulas_cached_only"]}
["文件号  DOC.NO:",{"$nulls":3},"第二批辅机设备清单"]
["序号\nNo.","设备位号\nItem No.","代 码\nCode","设备名称\nName","规   格\nSpecification","型号或图号\nModel Or\nDWG. No.","单位\nunit","数  量 QT'Y",null,null,"材 料\nMaterials","净重（kg) Net Weight",null,"数据表编号\nData Sheets No.","管口方位图编号\nNozzle Orientation \nDWG. No.","备  注\nRemarks"]
[{"$nulls":7},"设计\nDES.","备用\nSP.","请购\nREQ.",null,"单 重Single","总  重  Total"]
["一、锅炉部分",null,null," "]
[2,102,null,"鼓风机",null,null,"台",1,0,1]
[{"$nulls":3},"全压:4278"]
[{"$nulls":3},"流量:57918m3/h"]
[{"$nulls":3},"附防爆电动机（变频电机）",{"$nulls":3},1,0,1]
[{"$nulls":3},"功率:130KW（估算）"]
[{"$nulls":3},"电压:380V"]
[3,103,null,"引风机",null,null,"台",1,0,1]
[{"$nulls":3},"全压:4330Pa"]
[{"$nulls":3},"流量:93371m3/h"]
[{"$nulls":3},"附防爆电动机（变频电机）",null,null,"台",1,0,1]
[{"$nulls":3},"功率:160kW"]
[{"$nulls":3},"电压:380V"]
[4,104,null,"增压风机",null,null,"台",2,0,2]
[{"$nulls":3},"全压:4.5KPa"]
[{"$nulls":3},"流量：15000NM3"]
[{"$nulls":3},"附防爆电动机（变频电机）",null,null,"台",2,0,2]
[{"$nulls":3},"功率:（厂家计算）"]
[{"$nulls":3},"电压:"]
[{"$nulls":3},"介质:荒煤气"]
[null,"二、汽轮机部分"]
[22,222,null,"凝结水泵",null,null,"台",2,1,2]
[{"$nulls":3},"扬程:50--60MH2O"]
[{"$nulls":3},"流量:50t/h"]
[{"$nulls":3},"附电动机",null,null,"台",2,1,2]
[{"$nulls":3},"电压:380V"]
[{"$nulls":3},"功率:(厂家计算)"]
[23,223,null,"水环真空泵",null,null,"台",2,1,2]
[{"$nulls":3},"吸入压力:8KPa"]
[{"$nulls":3},"单抽吸干空气量：18.3kg/h"]
[{"$nulls":3},"单抽吸水蒸气量：18.8kg/h"]
[{"$nulls":3},"真空系统容积：130+排汽器和汽机排汽系统"]
[{"$nulls":3},"附电动机",null,null,"台",2,1,2]
[{"$nulls":3},"电压:380V"]
[{"$nulls":3},"功率:"]
[24,224,null,"大气式除氧器",null,null,"台",1,0,1]
[{"$nulls":3},"最大出力:50t/h"]
[{"$nulls":3},"工作压力:0.12MPa（绝压）"]
[{"$nulls":3},"出水温度:104℃"]
[{"$nulls":3},"运行方式：定压"]
[25,"225A/B",null,"电动给水泵",null,null,"台",1,1,2]
[{"$nulls":3},"流量:50t/h"]
[{"$nulls":3},"扬程:640m"]
[{"$nulls":3},"附电动机",null,null,"台",1,1,2]
[{"$nulls":3},"功率:（厂家计算）"]
[{"$nulls":3},"电压:"]
[26,226,null,"电动双钩桥式起重机",null,null,"台",1,0,1]
[{"$nulls":3},"20/5t   跨度13.5m  H=12.5M"]
[{"$nulls":3},"操作室悬挂式"]
[null,"三、化学水系统"]
[{"$nulls":3},"除盐水系统（EPC）",null,null,"套",1,0,1]
[{"$nulls":3},"过滤器+RO+混床系统"]
[{"$nulls":3},"制水量5t/h"]
[{"$nulls":3},"锅炉加药系统（45t/h，3.9MPa）",null,null,"套",1,0,1]